Demolition Scope of Work.   Demolition of space, including re-strapping / support of remaining cabling, conduit, VAV boxes, light fixtures, etc., must comply with all City of L.A. Building Code requirements.  Building permits are required.  It will be necessary to patch all fireproofing and rated partition penetrations as required by code.  In areas where demolition of existing walls or ceiling occurs, all existing kicker studs, braces and abandoned wires and piping above ceiling must be removed and the Monocot fireproofing must be repaired.  All demolition work (of any nature) shall be scheduled with the Building Management Office (BMO) during off-hours and at minimal disruption to the building’s operations and adjoining Tenants.  Use of the request for building services form, properly approved, available from the BMO, is required to properly communicate details and schedules of planned work.  Building Engineers must be notified and given an opportunity to inspect and approve work (especially above the ceiling line) at the conclusion of demolition.

Adjacent Tenant Space.   Demolition plans must provide detailed instructions for dealing with electrical, fire / life safety, HVAC, plumbing and any items that cross into adjacent tenant space (above, below and neighboring on same floor).  A complete survey of existing site conditions is required during the planning phase.  Consideration must be given to minimizing disruption to adjacent tenants by combining removal of abandoned items at the same time as installation of new thereby reducing the number of trips.  If access is required to adjacent Tenant space, forty-eight (48) hours advance notice to the BMO is required.  Use the designated request for building services form and clearly identify all areas where access is required with a detailed description of exactly what work will be performed and the impact on the adjacent Tenant.  Access times and dates will be at the discretion of the adjacent Tenant.  Contractor must be accompanied by either Building Engineer(s) or Security Officer(s) at all times while working in adjacent Tenant spaces. Extreme care must be taken by Contractor to protect and thoroughly clean the Tenant’s property following access daily before normal working hours.

Disturbance.   There shall be no construction or demolition work which generates noise, dust, obstruction, pollution, odors, fumes or any other disturbance to the quiet enjoyment of the building by tenants between 7:00 AM and 7:00 PM, every weekday including Saturdays & Sundays, without prior written approval from the BMO.

Disposal.   All demolition debris including rubbish and trash must be removed from the construction site at the end of each working day and disposed of in a safe manner. Under no circumstances will Contractor be allowed to use the Building’s trash dumpsters or compactors for demolition debris.  All demolished items and Debris must be removed from the property by the Contractor daily.  Contractor may arrange for a dumpster to be used on loading docks at nights and weekends.  Dumpsters must be delivered after 6:00 PM daily and removed from the property no later than 6:00 AM the following business day. All haulers must be duly licensed and/or franchised in the city in which the dumpster is located and must furnish proof of licensing or franchise agreement to BMO upon request.

Recycling. All materials must be recycled to the fullest extent possible, with a minimum of 75% diversion. Diversion reporting must be supplied to BMO at completion of demolition and proof of diversion should be provided by commodity. Proof of recycling must be provided for Ceiling Tile, Carpet, and Gypsum Drywall. Any building items that are suitable for reuse shall be made available for reuse by the contractor. Proof of any donation shall be provided to BMO upon request.

Building Rules and Regulations for Contractors and Contractor Guidelines.

All contractors and subcontractors must be pre-approved by the BMO prior to performing any work or services.  This approval is dependent upon many factors including the Contractors being properly licensed, insured, skilled and experienced in the work or services to be undertaken.  Each contractor must agree to the terms and conditions contained in the Building Rules and Regulations for Contractors, the Contractor Guidelines and acknowledge receipt of same, including the Landlord’s Hold Harmless / Indemnification Agreement before becoming an approved Contractor. Contractor will at all times provide on-site supervision for all workers and will manage compliance to the Building Rules and Regulations for Contractors and Contractor Guidelines.

- Hazardous Materials

- For all work performed, Contractor shall comply with all applicable federal, state and local laws, ordinances and regulation and lawful orders of public authorities (collectively “Hazardous Material Laws”)

- Any Freon containing devices must have the refrigerant evacuated by certified refrigerant recovery technicians and proof of evacuation must be presented to BMO. (https://www.arb.ca.gov/cc/rmp/rmptech.htm) This refrigerant recovery may take place onsite or at a recycling facility, so long as Federal, State and Local requirements are observed. Should the device be sent to a recycling facility for recycling, the General Contractor must have the device safed off and ensure that all refrigerant is pumped to the high side of the device for future removal. General Contractor must then obtain and provide proof of legal evacuation of refrigerant to BMO.

- Pursuant to the 2017 Cal-Green update contractors must submit a Universal Waste Management Plan. Per building code this plan will detail all California Covered Universal Waste located in the Tenant Space and include a recycling plan for these materials. At the completion of the project the contractor shall deliver to the BMO proof of recycling of all California Covered Universal Waste removed from the project. (For a list of California Covered Universal Waste  -  http://www.dtsc.ca.gov/HazardousWaste/UniversalWaste/upload/UW_Factsheet1.pdf) Failure to provide proof of diversion of identified Universal Waste may result in the project not receiving a final sign off for the permit.

- At its own expense, Contractor will procure, maintain in effect and comply with all conditions of any and all permits, licenses and other governmental and regulatory approvals required for all work performed by Contractors, including and without limitation, discharge of appropriately treated materials or wastes into or through any sanitary sewer servicing the property.

- Except as discharged into the sanitary sewer in strict accordance and conformity with all applicable Hazardous Materials Laws, Contractor will cause any and all Hazardous materials removed by it from the property to be removed and transported solely by duly licensed haulers to duly licensed facilities for final disposal or recycling of such materials and wastes. Contractor must make records of proper hauling and disposal of hazardous materials available to BMO at completion of project

- Contractor will in all respects handle, treat, deal with and manage any and all Hazardous Materials in, on, under or about the property in total conformity with all applicable Hazardous Materials laws and prudent industry practices regarding management of such Hazardous Materials including, but not limited to the proper presentation and display of Material Safety Data Sheets (“MSDS”). Upon completion of work, Contractor will cause all Hazardous Materials placed on, under or about property by Contractor or at Contractors direction to be removed and transported for use, storage, recycling or disposal in accordance and compliance with all applicable Hazardous Materials Laws.

B.	Required Contract Documents:

- Detailed Demolition Drawings Approved by Landlord.

- Written Demolition Specifications.

- Letter of Proposal from Demolition Contractor.

- Construction Waste Management Plan.

- Universal Waste Management Plan

- Landlord Approval of Demolition Contractor and all Subcontractors.

- Conditions of Proposal Approved by Landlord.

- Proposed Diversion Estimate

- Demolition plans must specify, and contractors must work to the following scope of work:

- Restrooms (tile floor, wall sinks, ceilings, etc.) will be protected from damage by use of Masonite and/or wall protections.  Wrap partitions to protect paint.

- Elevator lobby and corridor will be protected from damage by use of Masonite and/or wall protections.

- Protect freight elevator doors, walls, cabs, ceilings and frames.  Use doorframe protection at freight elevator corners.  Contractor may not use passenger elevators for any purpose unless there is no freight elevator available for use during off hours, and only at the discretion of the BMO. Should the passenger elevators be used for the removal of debris, said elevators must be fully protected in the same manner as a freight elevator with the addition of Masonite at the elevator floor.

- Protect existing loading dock area including floor and walls around dumpster. At the end of the nightly demolition shift all areas of the loading dock and path of travel are to be broom swept and/or washed down so there is no trace of debris within the building.

- On multi-tenant floors, protection in common areas must be removed no later than 7:00 AM before the next business day.

- Bag perimeter window covering to keep clean and protect from damage.  Use only low-tack (blue) tape.  Report if coverings are missing or damaged.

- Application of tape with strong adhesives must be limited to only items that are being removed from the property.  Do not apply duct or masking tape to any building elements that are to remain after the demolition process.

- Protect carpet at corridor where carpet is to be reused with carpet mask, plastic, and/or Masonite.

- Protect with plastic all existing wall covering at corridor and interior offices where existing walls are to remain.

- Protect return airshaft during demolition. Either block the shaft or install clean air filters daily.

- Demolition of fire / life safety equipment including smoke detectors, speakers, pull stations, strobes, magnetic door holders, etc., must be first surveyed and marked by the Landlord’s fire alarm service company.  Contact the BMO to arrange this function. The service company must identify exactly what fire/life safety equipment should be removed vs. braced, left in place and tied off.  Should this function not be accomplished, no demolition of these systems will be performed until the survey and marking are completed. Critical items are identified below:

  - All core devices must remain operational.

  - Fire rating integrity of all elevator lobbies, elevator shafts, stairways and remaining fire corridors must be maintained. Should fire corridor doors call to be removed on the demolition plan, said doors will be left in place until such time as the opening can be immediately sealed.

  - Pull stations at each stairwell and all elevator lobbies must remain operational.

  - The smoke detectors in each elevator lobby must remain operational including elevator recall.

  - Any electromagnetic door holders on elevator lobby doors and fire corridor doors must have active smoke detection left in place and must be operational to release doors in case of fire alarm activation.

  - Minimum fire alarm and voice evacuation speakers must be maintained in each elevator lobby, restroom and each quadrant of the floor. These systems must be tied off at a level of at least eight (8) feet off the finished floor.

  - Fire sprinkler systems throughout the floor must remain operational at all times except when sprinkler sub-contractor workers are present.

  - Water flow and tamper switch monitors on the fire sprinkler system must remain operational.

  - Duct detectors for base building HVAC Systems and smoke detectors in mechanical and electrical rooms must remain operational.

  - Configure strobe power supplies for the fire alarm system so that abandoned circuits do not cause trouble conditions from occurring on the system. This should only occur after survey and marking are successfully completed.

  - Exit signs and temporary lighting must be hard wired to emergency power at a level at least eight (8) feet above finished floor.

  - Fire doors must not be left open or missing at the conclusion of daily demolition.

  - Fire exits must remain unblocked and free of debris at all times.

- Fire sprinklers are to be left untouched in accordance with Building and Fire Code requirements.  Extreme care must be exercised to protect against accidental activation of sprinkler heads. All demolition personnel must make themselves aware of the location of sprinkler shut off valves prior to commencement of demolition.

- Retain existing emergency lighting and exit signs, properly braced for use on a temporary basis until new ceiling is provided on each floor. Lights are to be braced at least eight (8) feet above finished floor and Exit signs must be clearly visible.

- Remove all floor and ceiling tracks, kicker studs, braces, channels, etc. at the time they are exposed.  Remove any items hanging below eight (8) feet from the finished floor at the time exposed.  At no time will the contractor leave hanging items exposed overnight or between work periods.

- Remove all floor track fasteners (nails and bolts) as tracks are removed.  Fasteners must be removed or ground flat daily.

- Remove all existing data/voice cabling wiring/conduit occurring within the Tenant plenum space that is no longer in use, including service to floor mounted monuments on all floors.  NOTE: Do not remove cable, conduit and wires that services floors above and below floor of demolition or in adjacent tenant space on same floor. These cables, conduits, and wires are to be identified by the appropriate vendors prior to the commencement of demolition.

- Remove all Tenant related data/voice cabling/wire/conduit in building’s core electrical and telephone closets back to the electrical panels and backboard, including punch down blocks.  Protect all through-floor riser cabling (both voice and data) from damage.  If any question arises as to whether to demolish or save, cease work in this area until Contractor can contact the BMO for direction.  Existing sub-panels and transformers occurring in the electrical closets are to remain.

- All above ceiling support wires (ceiling hangers, wire hangers, etc.) are to be removed and clipped to within one (1) inch of deck.

- Electrical, mechanical and plumbing to be removed to the furthest termination point on the floor.

- Remove all unused and disconnected HVAC, electrical, plumbing and phone equipment above ceiling. These items are to be identified and marked by the appropriate vendors.

- Thermostats and pneumatic lines (if present) are to be removed in areas where demolition occurs and gently coiled up. If cut, damaged or removed, all lines must be plugged to avoid leaking and Building Engineers must be made aware of the damaged lines immediately

- Plumbing lines from below to be cut 12” above finish floor.  Temporarily cap open lines.

- Marked doors and frames to be sequentially numbered and carefully salvaged by neatly stacking them in the order of removal.

- Remove all wood, carpet, stone, or other existing Tenant floor finishes as called for in demolition plans.  Scrape concrete floor clean and return floor to its original condition.

- Do not at any time allow material and debris to generate and accumulate on the floor.  Remove daily and recycle or dispose of in a legal manner.

- Area of work to be cleaned (broom swept) every day.

- Dust barriers to be erected to prevent passage of debris or dust where needed. Dust barriers are to be maintained to ensure that they continue to provide protection.

- All personnel to be properly outfitted to proceed with work (hard hat, tools, boots, dust masks, etc.) and dressed in a professional manner. All personnel must wear clothing that clearly identifies the company they represent.

- Perform daily clean-up of existing corridors and restrooms.

- Perform daily clean-up of existing path of travel.

- Perform daily clean-up of loading dock and surrounding area.

- Perform daily removal of all debris from that day’s demolition work.